#### Converter MPC-110 (Code 702.046)

## Technical passport

Kaunas

© 2015

# Device purpose

- Read data from energy carrier meters (electricity, heat, water, GAS and other) with Mbus interface ;

- To store accounting and measuring data;

- Data exchange between device and client's software through GSM/GPRS.

# Device delivery set

- Converter MPC-110	1pc.

- Technical passport	1 pc.

- Software	1 pc.

# Technical data

##### Overall specification

CPU: 	ARM Cortex M4

Memory: archive storage 1-8 MB, battery backup, valid up to 5 years.

External memory: 	micro SD, up to 8GB

##### Interfaces

RS232:	up to 15m, speed up to 19,2 Kbits/s

RS485:	up to 1.2 km, max 32 transceivers, speed up to 19.2 Kbits/s

Mbus:	up to 25 devices (specify upon order), line auto-tune function, short-circuit protection

USB:	mini-B USB ver. 2.0

GPRS/GSM:  microSIM, 900/1800/1900 MHz

##### LED indication

Power

Mbus interface read/write and short circuit

GPRS status

##### Protocols

Modbus RTU, Modbus TCP/IP, IP, ICMP, UDP, TCP, DHCP, PPP, ARP, SNTP

##### General

Power supply AC:	90-250V ~ 50/60Hz

Power supply DC:	100-400V

Power consumption :	< 9VA

Interface galvanic isolation:	1000V

Real time clock:		Yes

##### Physical characteristics

Dimensions:	18x85x97 mm

Weight:	105 g

Case fixing type:	DIN35

Protection type:	IP20

##### Climate conditions

Operating temperature:	-25 .. +60oC

Storage temperature:	-40 .. +60oC

Humidity range:	5 – 95%, non- condensing

##### Programing and updating

Remotely: 	GPRS

Locally: 	USB

# Model code

# Model code explanation

##### 702.046.A.B.CA- First socket (UART1)

| 1 | RS485 |
| --- | --- |
| 2 | RS232 |
| 4 | M-bus |

B- SD card socket

| 0 | None |
| --- | --- |
| 1 | Micro SD |

C- Backup power

| 0 | None |
| --- | --- |
| 1 | Internal battery |

# Manufacturer warranty

Warranty period – 24 months.

In case of controller’s unavailability, the manufacturer commits to replace or carry out repair free of charges, if device was used in accordance with the operating manual.

A guarantee does not apply to faults caused by force majeure.

# Putting into operation certificate

##### Controller MPC-110

Model code: 702.046.4.1.0

Serial number:  86902

S.P.

Date of manufacturing:  November   2016

Controller is correctly assembled and completed.

The person responsible for certification: Rūta Mockutė